Makes eXcellent Incense Of Nature
Temp & Humi Controller	MEXION
MEX-150

Contents

❍ Part.1 Product description	5

❍ Part.2 General Instruction	6

❍ Part.3 Functions of the controller	7

❍ Part.4 Functions of the monitor button	8

❍ Part.5 Size of the product	9

❍ Part.6 Display Monitor	10

❍ Part.7 Boot	10

Read the setup figure of the body	10

Read the reciprocal data of the body	10

❍ Part.8 Operating equipment	12

Starting equipment	12

Stopping equipment	12

❍ Part.9 Operating conditions	13

Real time temperature/humidityStarting equipment	13

Ideal temperature/humidity	13

Operating conditions	13

Humidifier’s drainage and supply conditions	13

The auxiliary sensor and  condition of humidifier’s current	13

❍ Part.10 Basic settings - 1	14

Setting ideal temperature/humidity	14

Humidifier’s manual contro drainage and supply	14

❍ Part.11 Basic settings - 2	14

Set temperature/humidity deviation	15

Set delay time	16

❍ Part.12 Alarm check	16

❍ Part.13 Checking run-time	18

❍ Part.14 Modulation for the controller	19

❍ Part.15 Setting background	20

❍ Part.16 Product test	24

❍ Part.17 Setting the screen	23

❍ Part.18 Appendix electrode humidifier	24

❍ Part.19 Electrical network diagram	26

❍ Part.20 Warranty	28

Installation caution

Installation caution is for preventing of human

injuries or property damages in advance ,

so keep cautions mind and follow

them carefully carefully.

01	Do not test or inspect equipment when the power is off. Check the power before the test. | It can cause an electric shock.
02	Clean the equipment with a dry towel. | It can cause an explosion, modification or malfunction. When equipment is wet, stop operating it and dry the wet spot, 면with a cotton swab or ask the, head office for help.
03	Do not install in the same panel with high voltage devices.
04	Keep it more than 50mm away from peripheral modules or wiring ducts.
05	Do not disassemble or transform the equipment besides a service man. When the equipment doesn’t operate properly, ask the head office. It can cause a fire or an electric shock.
06	Do not use voltage whose capacity is above one of the rated voltage It can cause malfunction.
07	Do not put any material inside equipment. When dust or wiring dregs are inserted, it can cause malfunction.
08	Fix the equipment with incombustible materials such as a metal. | It can cause a fire
09	Do not put any material such as wiring dregs, welding materials, an iron, etc. It can cause malfunction, dysfunction or a fire.
10	Keep equipment indoors under natural ventilation conditions. Avoid direct ray of light and a place with high temperature and humidity as well as dust, gas, explosve gas, combustible gas and salinity. | It can shorten durability of equipment and also cause dysfunction.
11	When an input-output wire is put with a power line or a high tension wire, it can cause dysfunction or breakage followed by conduction disturbance.
12	After being fully aware of wiring, an expert deals with equipment. | It can cause a fire.
13	Do not use equipment after modification. | It can cause a fire.
14	Install duplex safety equipment in the place where possibility of human injury or property damage.
15	Put the controller and other devices (such as relay, inverter, contactor) in distance in order to prevent radiation noise or heat affection.
16	When concerned with noise filtration, use the noise filter or insulation trans.
17	Our controller containing enough counter measures can be used without a contactor except for the case of much noise. However, keep information mentioned below in mind for ground connection.
	• Use a suitable earthing device. • Use the third class of earthing device (earth resistance is below 100 Ohm) for construction. • Use a common earthing device in case a suitable one is not available

Part.1 Product description	MEXION	MEX-150

1. Product description

-  -

Monitor	Monitor	Body
Monitor	Room Senser	Duct Sensor
Manual	Monitor Cable	Sensor Cable

2.

Part.2 General Instruction	MEXION	MEX-150

General Instruction

1) Communication data(same for system bus and local bus)

- communication method : RS-485

- communication speed : 9600 BPS, N, 8, 1

- communication protocol : MODBUC RTU MODE

2) Construction

Conductor	bare copper strands
Insulation	PE(polyethylene)
Core code	with reference to DIN 47100
Stranding	2core tiwsted to pairs
Pair screen	plastic coated metal foil and dopper drain wire
Wrapping	plastic foil
Screen	braid dopper wire
Sheath	PVC, acc.to DIN VDE 0207 part5
Sheath colour	grey(RAl 7032)

3) Technical data

Peak operating voltage	250V
Testing voltage	C/C : 2000V
	C/S : 1000V
Min. bending radius	10 x d
Radiation resistance	8 x 107cJ/kg
Impedance	0.22 ㎟ approx. 80 Ohm
	0.34㎟ approx. 85 Ohm
	0.5 ㎟ approx. 80 Ohm
	1.0 ㎟ apporx. 75 Ohm
Capacitance	0.22 ㎟ max. 70 nF/㎞
	0.34 ㎟ max. 70 nF/㎞
	0.5 ㎟ max. 75 nF/㎞
	1.0 ㎟ max. 85 nF/㎞
	at 800Hz
Inductance	approx. 0.4mH/㎞
Temperature range	-30℃ to +70℃
Fire performance	IEC 60 332-1

※ This type of cable is recommended.

Part.2 General Instruction, Part.3 Functions of the controller	MEXION	MEX-150

4) Body (MeX-100)

Processor		ATmega32
Input voltage		80 ~ 245VAC Free-voltage *comm1)50/60Hz
Power	Voltage	80 ~ 245VAC
	Relay capacity	250V / 3A(MAX)
	DO port	14 Ports
	AO port	2 Ports (4~20mA, 0~10V 선택)
Input	Voltage	13VAC
	DI port	11 Ports
	AI port	2 Ports (4~20mA)
Communication	Method	RS-485, Modbus-RTU, (9600BPS,DATA 8, STOP1, PARITY NONE)
	Port	3 Ports (Monitor, sensor, exterior communication)

*comm1) The standard 60Hz, 50Hz is the order specifications.

5) Monitor(MoD-100)

Processor	ATmega128
Input voltage	DC 9 ~ 24V
Display	128 X 64 Mono Graphic LCD
Communication	1Ports, RS-485, Modbus-RTU, (9600BPS,DATA 8, STOP1, PARITY NONE)
Internal temperature sensor	DKSK103HF-NTC (-25.0 ~ 85.0℃ ±1.5℃)

6) Sensor (MeS-100)

Processor	ATmega8
Voltage	DC 9 ~ 24V
Communication	1Ports, RS-485, Modbus-RTU
Internaltemperature/humidity sensor	DKSK103HF-NTC (-25.0 ~ 85.0℃ ±1.5℃) / SHT10 (0 ~ 100.0 % ±4%)

3. Functions of the controller

1) Data protection

Data set in equipment is saved after a power failure

2) Remote check/control

All AHU controllers can be managed by CCU or PC

3) Functions of comparable power

The control point which manages an air-cooler, a air heater, a humidifier and a damper allows automatic/manual control.

4) Functions of comparable input

It can be set up to ideal controlling figures by getting exterior information on figures of temperature,humidity and pressure.

4.

Part.4 Functions of the monitor button	MEXION	MEX-150

Functions of the monitor button

	Operation/Stop :Use for Operating or stopping the equipment.
	Screen switch : Use for turning to next chapter or switching screen.
	Option : Use for saving or selecting real time figures.
	Up : Use for setting the selected menu up
	Down : Use for setting the selected menu down

This controller is designed to have a makeshift function inside with a micro processor control method and it can be connected to PC which makes it possible to be controlled  and managed its maintenance at once. Also, the monitor using Koean LCD is convenient for users to manage.

5.

Part.5 Size of the product	MEXION	MEX-150

Size of the product

6.

Part.6 Display Monitor, Part.7 Boot	MEXION	MEX-150

Display Monitor

1) When equipment starts running, it displays general running conditions such as real time temperature and humidity.

7. Boot

1) When the product operates for the first time, it downloads data of the body through the bootloader.

2) During power-on, downloaded data is saved and the boothloader reruns when the power is on again.

3) The raciprocal number on the body has spacific serial number which is set during the first download,

and this process is skipped from next time. (when the serial number on the body is different from the number on the monitor. download occurs again.)

4) When its communication with the body is disturbed, the monitor stays in the bootloader until communication succeeds and then no more process occurs.

▞Read the setup figure of the body

	[ Bootloader.1 ]
	• When receiving set numbers is finished, it displays PASS with the monitor and body program version 0.00D / 0.00M. • It moves to next step for receiving reciprocal information.

	[ Bootloader.2 ]
	• When its communication with the body is disturbed or 경우 received data is incorrect, it displays FAIL and continues to ask for correct data until it succeeds. • When a problem is detected, check the monitor connecting table.

Part.7 Boot	MEXION	MEX-150

▞Read the reciprocal data of the body.

	[ Bootloader.3 ]
	• It downloads reciprocal data of the body. • It displays processing rates each time when new data is updated.
	[ Bootloader.4 ]
	• When receiving reciprocal data is finished, it displays PASS and closes the bootloader.
	[ Bootloader.5 ]
	• When its communication with the body is disturbed or received data is incorrect, it displays FAIL and continues to ask for correct data until it succeeds • When a problem is detected, check the monitor connecting tables.
	[ Bootloader.6 ]
	• When all data is received, it closes the bootloader and displaysdownloaded name.

8.

Part.8 Operating equipment	MEXION	MEX-150

Operating equipment

▞Starting equipment

	[ Power.1 ]
	• When equipment stops operating, it displays this screen. • Pressing the power button for long time requests body operating.
	[ Power.2 ]
	• When the request is accepted, it displays delay time and counts down. • Pressing the select button closes the process by compulsion.
	[ Power.3 ]
	• When delay time is 0, it turns on starting condition and displays operating condition screen

▞Stopping equipment

	[ Power.4 ]
	• When equipment is running, it displays this screen. • Pressing the power button for long time requests for stop.
	[ Power.5 ]
	• When the request is accepted, it displays delay time and counts down. • Pressing the select button closes the process by compulsion.

9.

Part.9 Operating conditions	MEXION	MEX-150

Operating conditions

▞Real time temperature/humidity

	[ Status.1 ]
	• Real time temperature/humidity is displayed by receiving data from the temperature/humidity sensor which is connected to the body. • When the temperature/humidity sensor has a problem, the sensor alarm rings and displays 00.0 on the screen.

▞Ideal temperature/humidity

	[ Status.2 ]
	• It displays setup temperature/humidity numbers below real time temperature/humidity. • Setup numbers are the minimum condition for controller operation. • SP Stands for Set Point, T for temperature and H for Humidity.

▞Operating conditions

	[ Status.3 ]
	• It displays real time conditions of each device. • Conditions are displayed as a step(□) or rate(○○○%). • From the left step, it indicates 1step, blank - stop and the opposite - operation. • COOL, HEAT, HUMI, DEHU

▞ Humidifier’s drainage and supply conditions

	[ Status.4 ]
	• It displays humidifier’s drainage and supply conditions on the right corner. • WS indicates water drainage and DR indicates water supply.

▞ The auxiliary sensor and  condition of humidifier’s current

	[ Status.5 ]
	• When you press the down button on the main screen, it displays numbers of the auxiliary temperature sensor inside the monitor and current of the humidifier cylinder. • Current of the cylinder is displayed only when a pole type is selected. (Check CONFIG 5) • When you press the up button, it returns to the main screen.

10. Basic settings-1

Part.10 Basic settings-1, Part.11 Basic settings-2	MEXION	MEX-150

NO.	ITEM	RANGE	STEP	UNIT
1	Setup temperature	5.0~50.0	0.1	Temperature(℃)
2	Setup humidity	20~80	1	Humidity(%)

▞Setting ideal temperature/humidity

	[ Setup.1 ]
	• means ideal temperature setting and, ideal humidity setting. • When setting temerature and humidity, if you put the select button, , blink. Then you set temperature and humidity by up and down.

▞Humidifier’s manual contro drainage and supply

	[ Setup.2 ]
	• When the auxilary temperature sensor is on, if you press on/off down’, you can turn on/off the drain/supply valve manually. • If you press ‘select’, the selected valve’s mark blinks. ON In this mode, pressing ‘up’ leads ON output and ‘down’ OFF output. ※Be aware that it is manual operation.

11. Basic settings -2

1) When you press the screen change button, it displays basic settings screen.

2) Setting temperature-humidity deviation ↔ Changing to the page of delay time setup.

NO.	ITEM	RANGE	STEP	UNIT
1	Air-cooling deviation	0.1~10.0	0.1	Temperature(℃)
2	Air-heating deviation	0.1~10.0	0.1	Temperature(℃)
3	Humidity deviation	1.0~10.0	0.1	Humidity(%)
4	Dehumidification deviation	1.0~10.0	0.1	Humidity(%)
5	Operation delay	1~180	1	Second
6	Stop delay	1~180	1	Second

▞

Part.11 Basic settings-2	MEXION	MEX-150

Set temperature/humidity deviation

	[ Setup.3 ]
	• When you press the select button on the temperature/humidity deviation set page, it can be set up. • Set up ideal cooling-heating temperature deviation by pressing the up/down button. • When setup is done, press the select button in order to save changes. (move to next step) • Set air heating, humidification and dehumidification step n the same way.

※ Air cooling-heating temperature deviation means the condition of  air-cooler operation.

• Interior temperature  >= (ideal temperature) ＋ (temperature deviation x 1) =====> The cooler 1 operates.

• Interior temperature  >= (ideal temperature) ＋ (temperature deviation x 2) =====> The cooler 2 operates.

• When it’s a comparison =====>Power(%) = (interior temperature – setup temperature) ÷ temperature deviation X 100(%)

※ Air cooling-heating temperature deviation means the condition of air-cooler operation

• Interior temperature <= (ideal temperature) ― (temperature deviation × 1) =====>The heater 1 operates.

• Interior temperature <= (ideal temperature) ― (temperature deviation × 2) =====>The heater 2 operates.

• Interior temperature <= (ideal temperature) ― (temperature deviation × 3) =====>The heater 3 operates.

• terior temperature <= (ideal temperature) ― (temperature deviation × 4) =====>The heater 4 operates

• Interior temperature ==> Power(%) = (interior temperature  - setup temperature) ÷ temperature deviation  X 100(%

※ Humidity deviation means the condition of humidifier operation.

• Interior humidity  <= (ideal humidity) ― (humidity deviation × 1) =====> The humidifier 1 operates

• Interior humidity  <= (ideal humidity) ― (humidity deviation × 2) =====> The humidifier 2 operates

• When it’s a comparison ==>  Power(%) = (interior humidity - setup humidity) ÷ humidity deviation  X 100(%)

※ Dehumidification deviation means the condition of dehumidifier operation.

• Interior humidity  >= (ideal humidity) ＋ (dehumidification deviation x 1=====>  The dehumidifier 1 operates.

• Interior humidity  >= (ideal humidity) ＋ (dehumidification deviation x 2)=====>  The dehumidifier 2 operates.

• When it’s a comparison ==> Power(%) = (interior humidity – setup humidity) ÷ dehumidification deviation  X 100(%)

Part.11 Basic settings–2 settings-2, Part.12 Alarm check	MEXION	MEX-150

▞Set delay time

	[ Setup.4 ]
	• When you press the down button on the screen of setting temperature/humidity deviation, it displays the screen of setting delay time. • When you press ‘select’, numbers of operation delay blinks and you can set operation delay time.delay blink and it becomes possible to set up delay time. • When you press the select button in the mode of setting operating delay time, numbers of stop delay blink and it becomes possible to set up ideal numbers. • Set stop delay in the same way.

※ Setting delay time is for preventing an unexpected load by stopping simultaneous running of more than two devices.

※ Setting stop delay time is for emanating interior heat of running equipment

12. Alarm check

▞When you press the screen change button on the screen of setting basic operation, it displays the screen of alarm check.

▞Display alarm

	[ Alarm.1 ]
	• It displays real time alarm information. • Without a problem, it displays [No alarm information].

	[ Alarm.2 ]
	• It displays detailed information when an alarm rings. • Total number of occurred alarms is displayed on[TOTAL ALARM] section • Maximum 3 alarm messages can be displayed.

Part.12 Alarm check	MEXION	MEX-150

	[ Alarm.3 ]
	• When you press the select button for long time, it displays cancelling alarm mode by compulsion. • The button up is for deleting, down is for cancelling deleting and returning to the alarm check screen.
	[ Alarm.4 ]
	• On the screen of alarm check, if you press up/down, the screen of alarm occurrence/cancellation is displayed. • Maximum 30 alarm records can be shown.
	[ Alarm.5 ]
	• On the screen of alarm log, if you press ‘select’ for long time, it displays alarm cancellation mode • The ‘up’ button is for deletion, and ‘down’ is for cancellation of deleting alarm and it returns to the alarm check screen.

Part.12 Alarm check Part.13 Checking run-time	MEXION	MEX-150

※ Alarm message

Blower	Airflow or trip of ventilator MG detects a problem and it stops generating energy. (automatic recovery)
Comp 1	Problems occur when MG stops operating due to high or low pressure or trip of a overload safety device. (manual recovery)
Comp 2	Problems occur when MG stops operating due to high or low pressure or trip of a overload safety device. (manual recovery)
Heater	Problems occur when T.C is revealed due to overheating.
Humidifier	Problems occur when T.C is revealed or high tension current is detected. (automatic recovery)
Fire	When smoke or a contact sign is detected, all devices stop operating. (automatic recovery
Water leak	Problems occur when a leakage sensor detects moisture. (automatic recovery)
Water level	Problems occur when water level is abnormal. (automatic recovery)
Water supply	Problems occur when water supply of the humidifier is abnormal. (automatic recovery)
Drain	Problems occur when water drainage of the humidifier is abnormal.(automatic recovery)
Sensor	Problems occur when the sensor doesn’t respond due to communication failures or malfunction of the sensor. (automatic recovery)
High temp	When real time temperature is higher than the setup high temperature. (automatic recovery)
Low temp	When real time temperature is lower than the setup low temperature. (automatic recovery)
High -humi	When real time humidity is higher than the setup high humidity. (automatic recovery)
Low humi	When real time humidity is lower than the setup low humidity. (automatic recovery)

13. Checking run-time

1) When you press the screen change button, it displays the screen for checking run-time .

▞Display run-time

	[ Runtime.1 ]
	• Run-time of each device is recorded • It records and saves information in order of date and time

Part.13 Checking run-time, Part.14 Modulation for the controller	MEXION	MEX-150

	[ Runtime.2 ]
	• When you press the select button for long, it changes to the mode for cancelling run-time by compulsion • The button up is for deleting and the button down is for cancelling deleting and returning to the run-time screen

	[ Cur-Srare.1 ]
	• On run-time check screen [Run Time.1], if you press ‘up’ or ‘down’, it displays current setup. • Current step, revision status, and the number of equipment are shown.

14. Modulation for the controller

1) When you put equipment still and press the screen switch button for long time, it displays the screen for setting detailed functions of the device and  the controller.

2) Select the menu in order of setting backgrounds → checking the product → setting screens.

3) When a menu is selected, move to next page for setting details

4) This mode is only for equipment experts and a user’s changing the mode by himself can cause     malfunction or breakdown of the equipment.

▞Movement and entry among menus

	1. CONFIG [setting environment]
	• The first selected menu • Setting details for operating equipment • Move to next step by pressing the select button • Move to next menu by pressing the screen switch button

	2. I/O TEST [checking products]]
	• Press the screen switch button on the setting backgrounds screen • Check input/output of the controller • Move to next step for setting details by pressing the select button • Move to next menu by pressing the screen switch button

Part.14 Modulation for the controller, Part.15Setting background	MEXION	MEX-150

	3. DSPLAY [setting screens ]
	• Press the screen switch button on the checking products screen screen • Set monitors • Move to next step for setting details by pressing the select button • Move to next menu by pressing the screen switch button

15. Setting background

1) Set detailed environment for operating equipment

2) Move pages by pressing the up/down buttons

3) When you press the select button,  it becomes possible to set up and a selecteditem bilnks.

NO.	Item	Range	STEP	Unit
1	Air-cooling step	0(No use)/1~3/Ratio	1	STEP
2	Air-heating step	0(No use)/1~4/Ratio	1	STEP
3	Humidification step	0(No use)/1~2/Ratio	1	STEP
4	Dehumidification step	0(No use)/1~3/Ratio	1	STEP
5	Temperature revision	-10.0~10.0	0.1	Temperature(℃)
6	Humidity revision	-30.0~30.0	0.1	Humidity(%)

NO.	Item	Range	STEP	Unit
7	High temperature alarm	Prohibition/25.0~50.0	0.1	Temperature(℃)
8	Low temperature alarm	Prohibition/5.0~20.0	0.1	Temperature(℃)
9	High humidity alarm	Prohibition/60.0~90.0	0.1	Humidity(%)
10	Low Humidity Alarm	Prohibition/10.0~40.0	0.1	Humidity(%)
11	Air-cooler operation delay	1~180	1	Second
12	Air-cooler stop Delay	1~180	1	Second
13	Air-cooler alarm Delay	1~180	1	Second
14	Air-cooler reoperation delay	1~180	1	Second
15	Humidification method	General/Electrode
16	Drain period of humidifier	0~200	1	Hour
17	Drain time of humidifier	0~10	1	Minutes
18	Voltage of humidifier	220/380/440		Voltage(V)
19	Capacity of humidifier	3~45	1	kg/h
20	Current revision of humidifier	-3.0~3.0	1	Current(A)
21	The number of equipment	1~50	1	Number
22	Comparison period of air-cooler	0(No use)/1~120	1	Seconds
23	Comparison period of air-heater	0(No use)/1~120	1	Seconds
24	Comparison period of humidification	0(No use)/1~120	1	Seconds

Part.15 Setting background	MEXION	MEX-150

▞Setting equipment steps

	[ Config.1 ]
	• On equipment steps setting screen, if you press ‘select’, the number of air-cooling step blinks. • Set up ideal numbers by pressing the up/down button • Save changed numbers by pressing the select button (move to next step) • Set dehumidification, air heating, humidification in the same way.

※ Comparable capacity generates energy through AO-1 and AO-2 terminals. Thus, up to 2 can be set and when more than 2 are set, only allocated energy in the priority order can be

used. The priority order is air-cooling(dehumidification) -> air heating -> humidification.

※  If there’s no comparison setup, current temperature(0~100%),current humidity(0~100%) are used as basic comparison output. (For recorder output)

▞Correcting temperature/humidity

	[ Config.2 ]
	• Correcting temperature in the temperature/humidity sensor • Set in the same way as equipment step

▞Setting temperature/humidity alarm

	[ Config.3 ]
	• Alarm rings when higher or lower temperature than set temperature and humidity is sensed • Ban mark indicates blocking the chosen alarm. • Set in the same way as equipment steps.

▞Setting air conditioner delay

	[ Config.4 ]
	• Air-cooler operation delay: Set MG-ON output delay of air-cooler operation. • Air-cooler stop delay: Set MG-OFF output delay of air-cooler stop. • Air-cooler alarm delay: Set input time of air-cooler alarm. • Air-cooler reoperation dely: Set delay time of reoperation after the air-cooler stops running • Set in the same way as equipment steps.

Part.15 Setting background	MEXION	MEX-150

▞Setting humidifier  - types of humidifier

	[ Config.5 ]
	• Set a type of humidifier • Set in the same way as equipment steps.

▞Setting humidifier – drainage period and time

	[ Config.6 ]
	• Set drainage period and time • Set in the same way as equipment steps.

※ Setting pole peak is displayed only when humidifier type is set for pole setup.

▞ Setting humidifier in the pole peak – voltage

	[ Config.7 ]
	• Set humidifier voltage • Set in the same way as equipment steps.

▞Setting humidifier in the pole peak  - capacity

	[ Config.8 ]
	• Set humidifier capacity • Set in the same way as equipment steps.

▞Setting electrode humidifier

	[ Config.9 ]
	• Correct current in the cylinder of the electrode humidifier. • Set in the same way as equipment steps.

Part.15 Setting background	MEXION	MEX-150

▞Setting number of equipment

	[ Config.10 ]
	• Set number of equipment. The number is used as ID for communication with the remote monitoring system • Set in the same way as equipment steps.

▞Setting Proportion Period

1) When SSR(Soild State Relay)is used, setting proportion period

	[ Config.11 ]
	• Set cool proportion period • Set up ideal numbers by pressing the up/down button • Save changed numbers by pressing the select button (move to next step) Maximum ratio is 2 point so if you set the mode as the screen displays, it chooses air-cooling (dehumidification) and the others in dehumidification-heating-humidification order • For further information, please ask directly our corporation

▞Setting Reservation Runing

1)When you run/stop device by reservation run/stop time setting reservation time classified by a day of the week.

	[ Config.12 ]
	• Run time of sunday is blinking by pressing the select button • Set up ideal run time of Sundqy by pressing the up/down button • You con change by 30 minutes step • Complete setting by pressing the select button run time value of Sunday is saved in the EEPROM (Automatically moved to next item, automatically released by passing some times) * Setting reservation run/stop time classified by a day of the week by being above operation repeatdly. * If you do not reservation run on special day press the select butten, When “”is displayed on the screen by pressing the up button

Part.15 Setting background	MEXION	MEX-150

Part.16 Product test , Part.17 Setting the screen Part	MEXION	MEX-150

16. Product test

1) The mode is for testing input/output of the controller.

2) When you press the select button, a cursor blinks and changes to the test mode.

3) The button up is for ON and the button down is for OFF.

▞Output test

	[ IOtest.2 ]
	• Move a cursor by pressing the select button • Test output by pressing the up/down buttons after moving a cursor on the port you want to change • Input sends each port signal from the body and confirms displayed status

17. Setting the screen

1) Setting details related to monitor such as real time.

2) Move to other items by pressing the select button and apply set figure right away.

3) Change numbers by the pressing up/down button.

	[ Display.1 ]
	• Change numbers by pressing up/down button on a blinking item • Save changes by pressing the select button

18.

Part.18 Appendix electrode humidifier	MEXION	MEX-150

Appendix electrode humidifier

▞Product description

Model	Capacity	Voltage	Power consumption	Rated current	Size (H × W × L)(mm)
SYL-0A	3Kg/h	220V / 3Φ 380V / 3Φ 440V / 3Φ	2.3Kw 2.3Kw 2.3Kw	7.3A 4.2A 3.7A	Cylinder(Ducket) : 355 × 215 Trunk : 425 × 245 × 215
SYL-00	8Kg/h	220V / 3Φ 380V / 3Φ 440V / 3Φ	6Kw 6Kw 6Kw	19.6A 11.3A 9.8A	Cylinder(Ducket): 355 × 215 Trunk : 425 × 245 × 215
SYL-01	10Kg/h	220V / 3Φ	8Kw	24.4A	Cylinder(Ducket): 450 × 215 Trunk : 540 × 245 × 215
	15Kg/h	380V / 3Φ 440v / 3Φ	12Kw 12Kw	21.2A 18.3A
SYL-02	25Kg/h	220V / 3Φ	19Kw	61.1A	Cylinder(Ducket) : 540 × 310 Trunk : 800 × 390 × 360
	45Kg/h	380V / 3Φ 440v / 3Φ	34Kw 34Kw	63.7A 55.0A

▞Calculation of power consumption and humidification capacity

The most commonly used voltage in Korea is 380VAC(3Φ) and 220VAC(2Φor3Φ) thus supply voltage for installation of electrode humidifier is 380VAC or 220 VAC.

Energy efficiency is the highest and humidifier rating is the fastest with 3Φ voltage connection.Two models – SYL -00(8Kg/h) / SYL -01(15Kg/h) of electrode humidifiers can consume the high - est humidifier rating with 380VAC(3Φ) connection.

-Power consumption

P(W)`=` sqrt {3} `·`V`·`I`·(power factor)  (P:power, V:voltage, I:current)

Part.19 Electrical network diagram	MEXION	MEX-150

Part.19 Electrical network diagram	MEXION	MEX-150

Part.20 Warranty	MEXION	MEX-150

PRODUCT WARRANTY

Product : MEX-150

The product is warranted to the consumer for a period of 1 year from date

of retail purchase and warranty conditions are indicated below for details.

WARRANTY CONDITIONS

1. Product : MEX-150

2. Warranty period :  For a year (When purchase date is not checked, for 13     months from manufacture date

3 No warranty conditions

Damage or failure of equipment due to unsuitable environment or

usage which is not mentioned in the user manual.

Damage or breakdown caused by other products

Damage of failure of the equipment due to repair by a third party

which is not authorized or approved by our company

Damage caused by fire, explosion or weather condition

4. Replacement and delivery for A/S

User may need to bring a product for replacement directly to

the company

The company must pay for delivery charges in warranty period

The user must pay for delivery charges after warranty period is expired

The user must pay for delivery charges when a product doesn’t have a           problem

5. The guarantee is only applied to the product MEX-150. When organizing

systems or using products, users must consider of safety tems carefully.

MST Inc.

※ The product can be modified for improvement at any time.

※ For replacement or repair of the product due to malfunction or breakdown, please contact the head     company directly.

APPLYING FILEDS	MEXION	MEX-150

▞ CONTROLLER for temperature/humidity control  /  A thermo-hygrostat

▞ CONTROLLER for temperature control / An air conditioner

▞ F.F.U CONTROLLER

▞ Dry Cooler CONTROLLER

▞ CPU CHILER CONTROLLER

▞ CONTROLLER for low temperature storage

▞ CONTROLLER for a thermo dehumidifier

▞ CONTROLLER for a pyrostat

▞ CONTROLLER for a cooler / advanced, standard

▞ Remote control system for a thermo-hygrostat

▞ Remote control system for F.F.U / group, individual

▞ Electrode humidifier / interior, exterior

▞ Oil Cooler CONTROLLER

▞ HML automatic remote control monitor

▞ Temperature/humidity sensor for communication

▞ BFU CONTROLLER

▞ Air shower CONTROLLER

▞ CONTROLLER for a heat pump

▞ CONTROLLER for a vaporizing humidifier

※ We continue to develop and work on various controllers.

Please contact the head company or the development department when you have a

MST Corporation

198-6, Angok-ro, Bucheon-si, Gyeonggi-do, Republic of Korea

Tel. 032-343-2577~8 / Fax. 032-343-2579 / Mail. mst2577@hanmail.net / www.msti.co.kr